## BACnet Basic list - Nordic
Name | description | Object Type | Instance Number *Default | Priority (If any) | Access | Units | Range (Present value) | Basic control | Inputs | Outputs | Alarm
Comfort button | 0 = Ventilation mode Away after Away delay timer duration [Pintval,318]. Also overrides Room operating mode [Mval,42]. 1 = Ventilation mode according to Room operating mode [Mval,42]. | Binary Value | 50 | 13 | RW |  | [0 : Inactive ¦ 1 : Active] | X
Heat recovery ventilation state | Present Ventilation mode | Multistate Value | 361 |  | R |  | [ 1 : Off ¦ 2 : Away ¦ 3 : Home ¦ 4 : High ¦ 5 : Fume hood ¦ 6 : Fireplace ¦ 7 : Temporary high] ¦ ] | X
Room operating mode | Select Ventilation mode. Only works if Comfort button [Bval,50] = 1 If Comfort button [Bval,50] = 0, this register is Away. (If ventilation mode control is active on a digital input, the digital input overrides this register.) | Multistate Value | 42 | 13 | RW |  | [ 1 : Stop ¦ 2 : Away ¦ 3 : Home ¦ 4 : High] ¦ ] | X
Setpoint temperature when away | Different instance number depending on configured temperature controle: Supply air control (Sup) Extract air cascade control (Ext) | Analog Value | 1985 (Sup)* 1988 (Ext) |  | RW | °C | 10 to 30 | X
Setpoint temperature when home | Different instance number depending on configured temperature controle: Supply air control (Sup) Extract air cascade control (Ext) | Analog Value | 1994 (Sup)* 2070 (Ext) |  | RW | °C | 10 to 30 | X
Remaining time of fireplace ventilation |  | Analog Value | 2038 |  | R | min | 0 to 360 | X
Remaining time of rapid ventilation | Rapid ventilation = Ventilation mode Temporary High | Analog Value | 2031 |  | R | min | 0 to 360 | X
Fireplace ventilation runtime |  | Positiv Integer Value | 270 |  | RW | min | 0 to 360 | X
Rapid ventilation runtime | Rapid ventilation = Ventilation mode Temporary High | Positiv Integer Value | 293 |  | RW | min | 1 to 360 | X
Trigger temporary fireplace ventilation |  | Multistate Value | 360 |  | RW |  | [ 1 : Ready ¦ 2 : Trigger] ¦ ] | X
Trigger temporary rapid ventilation | Rapid ventilation = Ventilation mode Temporary High | Multistate Value | 357 |  | RW |  | [ 1 : Ready ¦ 2 : Trigger] ¦ ] | X
AWAY delay timer duration | Sets the delay time for Comfort button [Bval,50] | Positiv Integer Value | 318 |  | RW | min | 0 to 600 | X
Room air quality 1 | CO2 value from CI76 - CO2 sensor. Only exists if CI75 - Wireless adapter is configured. | Analog Value | 2096 |  | R | ppm | 0 to 2000 |  | X
Exhaust air fan speed feedback |  | Analog Input | 12 |  | R | rpm | 0 to 18000 |  | X
Supply air fan speed feedback |  | Analog Input | 5 |  | R | rpm | 0 to 18000 |  | X
Relative humidity for extract air | Only exists if configured on X3 | Analog Input | 50 |  | R | % | 0 to 100 |  | X
Extract air pressure | Only exists if Fan control is configured as duct pressure (CI80) | Analog Input | 72 |  | R | Pa | -3000 to 3000 |  | X
Supply air pressure | Only exists if Fan control is configured as duct pressure (CI80) | Analog Input | 73 |  | R | Pa | -3000 to 3000 |  | X
Exhaust air temperature |  | Analog Input | 11 |  | R | °C | -50 to 80 |  | X
Extract air temperature |  | Analog Input | 59 |  | R | °C | -50 to 80 |  | X
Frost protection temp.for heating coil | Only exists if Water heating is configured | Analog Input | 31 |  | R | Pa | -3000 to 3000 |  | X
Outside air temperature |  | Analog Input | 1 |  | R | °C | -50 to 50 |  | X
Room temperature | Temperature sensor on CI70 | Analog Input | 75 |  | R | °C | 0 to 50 |  | X
Room air humidity 1 | RH value from CI77 - RH sensor 1. Only exists if CI75 - Wireless adapter is configured. | Analog Value | 2093 |  | R | % | 0 to 100 |  | X
Room air humidity 2 | RH value from CI77 - RH sensor 2. Only exists if CI75 - Wireless adapter is configured. | Analog Value | 2094 |  | R | % | 0 to 100 |  | X
Room air humidity 3 | RH value from CI77 - RH sensor 3. Only exists if CI75 - Wireless adapter is configured. | Analog Value | 2095 |  | R | % | 0 to 100 |  | X
Room air quality input value (CU) | Only exists if configured on X3 | Analog Input | 50 |  | R | ppm | 0 to 2000 |  | X
Supply air temperature |  | Analog Input | 4 |  | R | °C | -50 to 80 |  | X
Away | Only exists if configured on DI1, DI2 or X8 | Binary Input | 22 (DI1) 29 (DI2) 31 (X8)* |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
CO detector | Only exists if configured on X8 | Binary Input | 87 |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Emergency off | Only exists if configured on X8 | Binary Input | 32 |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Fire damper feedback | Only exists if Fire damper is configured and fire damper feedback is selected on DI1, DI2 or X8 | Binary Input | 18 (DI1) 25 (DI2) 92 (X8) |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Fume hood ventilation input | Cooker hood. Only exists if configured on DI1, DI2 or CI79 | Binary Input | 16 (DI1) 23 (DI2)* 493 (CI79) |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Fireplace ventilation input | Only exists if configured on DI1 or DI2 | Binary Input | 17 (DI1) 24 (DI2) |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Heating coil overtemperature detector | Only exists if Electric heater is configured | Binary Input | 33 |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
High | Only exists if configured on DI1 or DI2 | Binary Input | 82(DI1)* 83 (DI2) |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Home | Only exists if configured on DI1, DI2 or X8 | Binary Input | 21 (DI1) 28 (DI2) 30 (X8) |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire exhaust fan operation | Only exists if configured on X8 | Binary Input | 88 |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire fan off operation | Only exists if configured on X8 | Binary Input | 90 |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire supply & exhaust fan op. | Only exists if configured on X8 | Binary Input | 91 |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire supply fan operation | Only exists if configured on X8 | Binary Input | 89 |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Stop | Only exists if configured on DI1 or DI2 | Binary Input | 20 (DI1) 27 (DI2) |  | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Cooling coil valve position | Only exists if Water cooling is configured and Water cooling valve is selected on X7 | Analog Output | 34 |  | R | % | 0 to 100 |  |  | X
Exhaust air fan speed |  | Analog Output | 4 |  | R | % | 0 to 100 |  |  | X
Supply air fan speed |  | Analog Output | 3 |  | R | % | 0 to 100 |  |  | X
Heating coil electric position | Only exists if Electric heater is configured | Analog Output | 29 |  | R | % | 0 to 100 |  |  | X
Heating coil valve position | Only exists if Water heating is configured | Analog Output | 12 |  | R | % | 0 to 100 |  |  | X
Rotary heat exchanger speed |  | Analog Output | 0 |  | R | % | 0 to 100 |  |  | X
Cooling coil pump command | Only exists if Water cooling or DX cooling is configured and Cooling pump is selected on Q1, Q2 or Q3 | Binary Output | 64 (Q1) 68 (Q2) 57 (Q3) |  | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
Outside air damper command | Only exists if Outside air damper is configured on Q1, Q2 or Q3 | Binary Output | 18 (Q1)* 65 (Q2) 69 (Q3) |  | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
Fire damper command | Only exists if Fire damper is configured and fire damper command is selected on Q1, Q2 or Q3. | Binary Output | 19 (Q1) 66 (Q2) 46 (Q3) |  | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
Heating coil pump command | Only exists if Water heating is configured | Binary Output | 58 |  | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
A-Alarm acknowledgement |  | Multistate Value | 344 |  | RW |  | [ 1 : Ready ¦ 2 : Acknowledge ¦ 3 : Reset] ¦ ] |  |  |  | X
A-Alarm code |  | Analog Value | 8 |  | R |  | 0 to 9999 |  |  |  | X
A-Alarm indication |  | Multistate Value | 343 |  | R |  | [ 1 : Normal ¦ 2 : Alarm] ¦ ] |  |  |  | X
A-Alarm state |  | Multistate Value | 7 |  | R |  | [ 1 : Acknowledged, unlocked ¦ 2 : Unacknowledged ¦ 3 : Locked] ¦ ] |  |  |  | X
B-Alarm acknowledgement |  | Multistate Value | 341 |  | RW |  | [ 1 : Ready ¦ 2 : Acknowledge] ¦ ] |  |  |  | X
B-Alarm code |  | Analog Value | 130 |  | R |  | 0 to 9999 |  |  |  | X
B-Alarm indication |  | Multistate Value | 340 |  | R |  | [ 1 : Normal ¦ 2 : Alarm] ¦ ] |  |  |  | X
B-Alarm state |  | Multistate Value | 18 |  | R |  | [ 1 : Acknowledged, unlocked ¦ 2 : Unacknowledged ¦ 3 : Locked] ¦ ] |  |  |  | X
Display fault list | Alarm code for current place in fault list | Analog Value | 2025 |  | R |  | 0 to 10000 |  |  |  | X
Fault counter | Number of alarms in fault list | Analog Value | 2026 |  | R |  | 0 to 2000 |  |  |  | X
Fault list number | Current place in fault list | Analog Value | 2027 |  | R |  | 1 to 10000 |  |  |  | X
Fault list operation | Operates the fault list. 3: Refresh, removes all inactive alarms. (All inactive alarms will also be removed if the product is powered down) | Multistate Value | 342 |  | RW |  | [ 1 : Ready ¦ 2 : Next fault ¦ 3 : Refresh] ¦ ] |  |  |  | X
Operating time filter |  | Analog Value | 285 |  | RW | h | 0 to 99999 |  |  |  | X
Operating time for filter replacement |  | Analog Value | 286 |  | RW | h | 0 to 99990 |  |  |  | X