## Modbus
Name | Description | Modbus address (Base 0) | Register Type | Data Type (Big endian byte order) | Function code | Access | Units | Range | Basic control | Inputs | Outputs | Alarm | WH4
System Status | Modbus registers only accessable during System Status: Operation mode | 4x9001 | Holding | Uint 16 | FC 03 | R |  | [0 : Operation mode ¦ 2 : Configuration mode] | x
Room temp.setpoint for heating circuit |  | 4x1451 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 0 to 50 | x |  |  |  | x
Comfort button | 0 = Ventilation mode Away after Away delay timer duration [4x1615]. Also overrides Room operating mode [4x2013]. 1 = Ventilation mode according to Room operating mode [4x2013]. | 4x2040 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [0 : Inactive ¦ 1 : Active] | X
Room operating mode | Select Ventilation mode. Only works if Comfort button [4x2040] = 1 If Comfort button [4x2040] = 0, this register is Away. (If ventilation mode control is active on a digital input, the digital input overrides this register.) | 4x2013 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Stop ¦ 2 : Away ¦ 3 : Home ¦ 4 : High] ¦ ] | X
Setpoint temperature when away |  | 4x1163 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 10 to 30 | X
Setpoint temperature when home |  | 4x1155 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 10 to 30 | X
Fireplace ventilation runtime |  | 4x1105 | Holding | Uint 32 | Read: FC 03 Write: FC 16 | RW | min | 0 to 360 | X
Rapid ventilation runtime | Rapid ventilation = Ventilation mode Temporary High | 4x1103 | Holding | Uint 32 | Read: FC 03 Write: FC 16 | RW | min | 1 to 360 | X
Trigger temporary fireplace ventilation |  | 4x3007 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Trigger] ¦ ] | X
Trigger temporary rapid ventilation | Rapid ventilation = Ventilation mode Temporary High | 4x3006 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Trigger] ¦ ] | X
AWAY delay timer duration | Sets the delay time for Comfort button [4x2040] | 4x1615 | Holding | Uint 32 | Read: FC 03 Write: FC 16 | RW | min | 0 to 600 | X
Remaining time of rapid ventilation | Rapid ventilation = Ventilation mode Temporary High | 3x1035 | Input | Float 32 | FC 04 | R | min | 0 to 360 | X
Remaining time of fireplace ventilation |  | 3x1037 | Input | Float 32 | FC 04 | R | min | 0 to 360 | X
Domestic hot water state | Current water mode | 3x3005 | Input | Uint 16 | FC 04 | R |  | [ 1 : Comfort ¦ 2 : Economy ¦ 3 : Not in use ¦ 4 : Temporary boost ¦ 5 : Forced charge ¦ 6 : Economy delay ¦ 7 : Legionella prevention] ¦ ] | x
Heat recovery ventilation state | Present Ventilation mode | 3x3034 | Input | Uint 16 | FC 04 | R |  | [ 1 : Off ¦ 2 : Away ¦ 3 : Home ¦ 4 : High ¦ 5 : Fume hood ¦ 6 : Fireplace ¦ 7 : Temporary high] ¦ ] | X
Plant operating mode for heat pump |  | 4x2061 | Holding | Uint 16 | FC 03 | R |  | [ 1 : Off ¦ 2 : Vent.heating from tank ¦ 3 : Load tank ¦ 4 : Load tank & vent.heating ¦ 5 : Space heating from tank ¦ 6 : Space heat.& vent.heat.from tank ¦ 7 : Load tank & space heat. ¦ 8 : Load tank & space heat.& vent. ¦ 9 : HP not available ¦ 10 : Swi-off delay flow through heat. ¦ 11 : Legionella prev.vent.heat. ¦ 12 : Legionella prev.space heat. ¦ 13 : Space heat.with HP ¦ 14 : Space heat.& vent.with HP ¦ 15 : Load tank & space heat.with HP ¦ 16 : Load tank & vent.& space with HP ¦ 17 : Legionella prev.tank] ¦ ] | x
Domestic hot water mode | Select water mode | 4x3017 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Comfort ¦ 2 : Economy] ¦ ] | x
Domestic hot water temporary boost | Use this to trigger water mode: Temporary boost with duration according to [4x1513] | 4x3019 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Start ¦ 3 : Stop] ¦ ] | x
Time for domestic hot water tmp.boost | Duration for water mode: Temporary boost | 4x1513 | Holding | Uint 32 | Read: FC 03 Write: FC 16 | RW | min | 0 to 300 | x
Flow temperature heating circuit | Space heating flow temperatur (Secondary water circuit) | 3x0097 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x |  |  | x
Return temperature heating circuit | Space heating return temperatur (Secondary water circuit) | 3x0101 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x |  |  | x
Outside air temperature |  | 3x0001 | Input | Float 32 | FC 04 | R | °C | -50 to 50 |  | X
Supply air temperature |  | 3x0005 | Input | Float 32 | FC 04 | R | °C | -50 to 80 |  | X
Extract air temperature |  | 3x0009 | Input | Float 32 | FC 04 | R | °C | -50 to 80 |  | X
Exhaust air temperature |  | 3x0013 | Input | Float 32 | FC 04 | R | °C | -50 to 80 |  | X
Supply air fan speed feedback |  | 3x0021 | Input | Float 32 | FC 04 | R | rpm | 0 to 18000 |  | X
Exhaust air fan speed feedback |  | 3x0025 | Input | Float 32 | FC 04 | R | rpm | 0 to 18000 |  | X
Supply air pressure | Only exists if Fan control is configured as duct pressure (CI80) | 3x0037 | Input | Float 32 | FC 04 | R | Pa | -3000 to 3000 |  | X
Extract air pressure | Only exists if Fan control is configured as duct pressure (CI80) | 3x0041 | Input | Float 32 | FC 04 | R | Pa | -3000 to 3000 |  | X
Room air quality input value | External Harness (117019) is required to connect a CO2 0-10V sensor. No Application configuration needed. | 3x0045 | Input | Float 32 | FC 04 | R | ppm | 0 to 2000 |  | x
Differential pressure supply air fan |  | 3x0053 | Input | Float 32 | FC 04 | R | Pa | -3000 to 3000 |  | x
Differential pressure exhaust air fan |  | 3x0057 | Input | Float 32 | FC 04 | R | Pa | -3000 to 3000 |  | x
Relative humidity for extract air | Only exists if configured on X3 | 3x0061 | Input | Float 32 | FC 04 | R | % | 0 to 100 |  | X
Condenser pump speed feedback | Primary water pump. | 3x0069 | Input | Float 32 | FC 04 | R | % | 0 to 100 |  | x
Domest.hot w.storage tank temp., top |  | 3x0081 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Domest.hot w.storage tank temp., middle |  | 3x0085 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Domest.hot w.storage tank temp., bottom |  | 3x0089 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Return temperature storage tank |  | 3x0093 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Heat pump fault code | Heat pump operational information | 3x0105 | Input | Float 32 | FC 04 | R | --- | 0 to 10000 |  | x
Flow temperature heat pump |  | 3x0109 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Flow temperature after reheating coil |  | 3x0113 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Return temperature heat pump |  | 3x0117 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Air inlet temperature heat pump | Heat pump operational information | 3x0121 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Deicing temperature heat pump | Heat pump operational information | 3x0125 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Discharge gas temperature heat pump | Heat pump operational information | 3x0129 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Heat sink temperature inverter | Heat pump operational information (x10 for correct value) | 3x0133 | Input | Float 32 | FC 04 | R | °C | -50 to 150 |  | x
Heat pump fan speed feedback | Heat pump operational information | 3x0137 | Input | Float 32 | FC 04 | R | Hz | 0 to 100 |  | x
Heat pump compressor speed feedback | Heat pump operational information | 3x0145 | Input | Float 32 | FC 04 | R | Hz | 0 to 100 |  | x
Room air quality input value (CU) | Only exists if configured on X3 | 3x0149 | Input | Float 32 | FC 04 | R | ppm | 0 to 2000 |  | X
Room air humidity 1 | RH value from CI77 - RH sensor 1. Only exists if CI75 - Wireless adapter is configured. | 3x1001 | Input | Float 32 | FC 04 | R | % | 0 to 100 |  | X
Room air humidity 2 | RH value from CI77 - RH sensor 2. Only exists if CI75 - Wireless adapter is configured. | 3x1003 | Input | Float 32 | FC 04 | R | % | 0 to 100 |  | X
Room air humidity 3 | RH value from CI77 - RH sensor 3. Only exists if CI75 - Wireless adapter is configured. | 3x1005 | Input | Float 32 | FC 04 | R | % | 0 to 100 |  | X
Room air quality 1 | CO2 value from CI76 - CO2 sensor. Only exists if CI75 - Wireless adapter is configured. | 3x1007 | Input | Float 32 | FC 04 | R | ppm | 0 to 2000 |  | X
High | Only exists if configured on DI1 or DI2 | 3x3006 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Home | Only exists if configured on DI1, DI2 or X8 | 3x3007 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Away | Only exists if configured on DI1, DI2 or X8 | 3x3008 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Stop | Only exists if configured on DI1 or DI2 | 3x3009 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Fireplace ventilation input | Only exists if configured on DI1 or DI2 | 3x3010 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Fume hood ventilation input | Cooker hood. Only exists if configured on DI1 or DI2 | 3x3011 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Fire damper feedback | Only exists if Fire damper is configured and fire damper feedback is selected on DI1, DI2 or X8 | 3x3013 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Emergency off | Only exists if configured on X8 | 3x3015 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
CO detector | Only exists if configured on X8 | 3x3016 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire exhaust fan operation | Only exists if configured on X8 | 3x3017 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire supply fan operation | Only exists if configured on X8 | 3x3018 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire fan off operation | Only exists if configured on X8 | 3x3019 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire supply & exhaust fan op. | Only exists if configured on X8 | 3x3020 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Heating coil overtemperature detector | Only exists if Electric heater is configured | 3x3023 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Heat pump state | Heat pump operational information | 3x3028 | Input | Uint 16 | FC 04 | R |  | [ 1 : Standby ¦ 2 : Air purge process ¦ 3 : Startup process ¦ 4 : Normal operation ¦ 5 : Stop process ¦ 6 : Defrost operation ¦ 7 : Standby when error ¦ 8 : Manual operation ¦ 9 : Forced fan operation ¦ 10 : Forced pump operation ¦ 11 : State 10 ¦ 12 : State 11 ¦ 13 : State 12 ¦ 14 : State 13 ¦ 15 : State 14 ¦ 16 : State 15] ¦ ] |  | x
Heat pump reheating coil overtemp.det. |  | 3x3029 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | x
Heat pump frost protection state | Heat pump operational information | 3x3031 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | x
Drain pan heater state | Heat pump operational information | 3x3036 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | x
Heat pump warning limescale | Heat pump operational information | 3x3037 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | x
Heating circuit pump speed |  | 4x0061 | Holding | Float 32 | FC 04 | R | % | 0 to 100 |  |  | x |  | x
Storage tank consumer valve position |  | 4x0057 | Holding | Float 32 | FC 04 | R | % | 0 to 100 |  |  | x |  | x
Cooling coil valve position | Only exists if Water cooling is configured | 4x0025 | Holding | Float 32 | FC 04 | R | % | 0 to 100 |  |  | X
Exhaust air fan speed |  | 4x009 | Holding | Float 32 | FC 04 | R | % | 0 to 100 |  |  | X
Supply air fan speed |  | 4x005 | Holding | Float 32 | FC 04 | R | % | 0 to 100 |  |  | X
Heating coil electric position | Only exists if Electric heater is configured | 4x0013 | Holding | Float 32 | FC 04 | R | % | 0 to 100 |  |  | X
Rotary heat exchanger speed |  | 4x0001 | Holding | Float 32 | FC 04 | R | % | 0 to 100 |  |  | X
Cooling coil pump command | Only exists if Water cooling or DX cooling is configured and Cooling pump is selected on Q1, Q2 or Q3 | 4x2004 | Holding | Uint 16 | FC 03 | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
Outside air damper command | Only exists if Outside air damper is configured on Q1, Q2 or Q3 | 4x2007 | Holding | Uint 16 | FC 03 | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
Fire damper command | Only exists if Fire damper is configured and fire damper command is selected on Q1, Q2 or Q3. | 4x2043 | Holding | Uint 16 | FC 03 | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
Exhaust air damper command |  | 4x2010 | Holding | Uint 16 | FC 03 | R |  | [0 : Inactive ¦ 1 : Active] |  |  | x
Heat pump connection damper position |  | 4x0029 | Holding | Float 32 | FC 04 | R | % | 0 to 100 |  |  | x
Heat pump exhaust air damper command |  | 4x2064 | Holding | Uint 16 | FC 03 | R |  | [0 : Inactive ¦ 1 : Active] |  |  | x
HP electric reheating coil power request | 0-100% control of 1kW or 3kW depending on selection during installation. | 4x0085 | Holding | Float 32 | FC 04 | R | % | 0 to 100 |  |  | x
Heat pump setpoint flow temperature |  | 4x0073 | Holding | Float 32 | FC 04 | R | °C | -50 to 150 |  |  | x
HP storage tank changeover valve cmd. |  | 4x2067 | Holding | Uint 16 | FC 03 | R |  | [0 : Inactive ¦ 1 : Active] |  |  | x
Heat pump thermic power output |  | 4x0065 | Holding | Float 32 | FC 04 | R | kW | 0 to 100 |  |  | x
Flow temp.setpoint for heating circuit | Currentsetpoint for space heating flow temperature (Based on heating curve, parallell shift and room setpoint) | 3x1055 | Input | Float 32 | FC 04 | R | °C | 0 to 100 |  |  |  |  | x
Setpoint corr.for flow temp.heat.circuit | Use this to shift the flow temperature for the enitre heating curve up or down. | 4x1449 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | K | -20 to 20 |  |  |  |  | x
Setpoint temp.difference for heat.circ. | This sets the delta between the flow and return temperature which the secondary pump (Space heating) aims to keep. | 4x1473 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | K | 1 to 20 |  |  |  |  | x
Max.flow temp.setpoint for heat.circuit | Sets the max limit for the flow temperature setpoint. | 4x1417 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 5 to 70 |  |  |  |  | x
Min.flow temp.setpoint for heat.circuit | Sets the min limit for the flow temperature setpoint. | 4x1419 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 5 to 70 |  |  |  |  | x
Outside air temp.limit for heating circ. | Outdoor temperature limit for activation of space heating. | 4x1415 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | -50 to 50 |  |  |  |  | x
Outs.air temp.limit elec.reh.heat.circ. | Outdoor temperature limit that allows electric heater to assist space heating. | 4x1467 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | -50 to 50 |  |  |  |  | x
Negative switching differential | Sets the on-hysteresis for space heating | 4x1609 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | k | 0 to 20 |  |  |  |  | x
Positive switching differential | Sets the off-hysteresis for space heating | 4x1611 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | k | 0 to 20 |  |  |  |  | x
Outs.air temp.limit stor.tank heat.circ. | Above this outdoor temperature limit, space heating uses energy from the hot water tank | 4x1617 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | -50 to 50 |  |  |  |  | x
Outs.air temp.limit HP direct heat.circ. | Below this outdoor temperature limit, space heating uses only heat pump. | 4x1619 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | -50 to 50 |  |  |  |  | x
Flow temp.setpoint 1 for heating curve | Flow temperature at outdoor temperature: -30 °C | 4x1423 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 5 to 95 |  |  |  |  | x
Flow temp.setpoint 2 for heating curve | Flow temperature at outdoor temperature: -20 °C | 4x1427 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 5 to 95 |  |  |  |  | x
Flow temp.setpoint 3 for heating curve | Flow temperature at outdoor temperature: -10 °C | 4x1431 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 5 to 95 |  |  |  |  | x
Flow temp.setpoint 4 for heating curve | Flow temperature at outdoor temperature: -5 °C | 4x1435 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 5 to 95 |  |  |  |  | x
Flow temp.setpoint 5 for heating curve | Flow temperature at outdoor temperature: 0 °C | 4x1439 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 5 to 95 |  |  |  |  | x
Flow temp.setpoint 6 for heating curve | Flow temperature at outdoor temperature: 5 °C | 4x1443 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 5 to 95 |  |  |  |  | x
Flow temp.setpoint 7 for heating curve | Flow temperature at outdoor temperature: 15 °C | 4x1447 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 5 to 95 |  |  |  |  | x
A-Alarm acknowledgement |  | 4x3002 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Acknowledge ¦ 3 : Reset] ¦ ] |  |  |  | X
B-Alarm acknowledgement |  | 4x3003 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Acknowledge] ¦ ] |  |  |  | X
A-Alarm code |  | 3x1021 | Input | Float 32 | FC 04 | R |  | 0 to 9999 |  |  |  | X
B-Alarm code |  | 3x1023 | Input | Float 32 | FC 04 | R |  | 0 to 9999 |  |  |  | X
Fault counter | Number of alarms in fault list | 3x1025 | Input | Float 32 | FC 04 | R |  | 0 to 2000 |  |  |  | X
Fault list number | Current place in fault list | 3x1027 | Input | Float 32 | FC 04 | R |  | 1 to 10000 |  |  |  | X
Display fault list | Alarm code for current place in fault list | 3x1029 | Input | Float 32 | FC 04 | R |  | 0 to 10000 |  |  |  | X
Fault list operation | Operates the fault list. 3: Refresh, removes all inactive alarms. (All inactive alarms will also be removed if the product is powered down) | 4x3004 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Next fault ¦ 3 : Refresh] ¦ ] |  |  |  | X
Operating time filter |  | 4x1271 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | h | 0 to 99999 |  |  |  | X
Operating time for filter replacement |  | 4x1269 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | h | 0 to 99990 |  |  |  | X
A-Alarm indication |  | 3x3001 | Input | Uint 16 | FC 04 | R |  | [ 1 : Normal ¦ 2 : Alarm] ¦ ] |  |  |  | X
A-Alarm state |  | 3x3002 | Input | Uint 16 | FC 04 | R |  | [ 1 : Acknowledged, unlocked ¦ 2 : Unacknowledged ¦ 3 : Locked] ¦ ] |  |  |  | X
B-Alarm indication |  | 3x3003 | Input | Uint 16 | FC 04 | R |  | [ 1 : Normal ¦ 2 : Alarm] ¦ ] |  |  |  | X
B-Alarm state |  | 3x3004 | Input | Uint 16 | FC 04 | R |  | [ 1 : Acknowledged, unlocked ¦ 2 : Unacknowledged ¦ 3 : Locked] ¦ ] |  |  |  | X